## Slide 1: Waste water Treatment by Anaerobic methods for a Dairy Processing Plant
Dr. J. Badshah
University Professor – cum - Chief Scientist
Dairy Engineering Department
Sanjay Gandhi Institute of Dairy Science & Technology, Jagdeopath, Patna
(Bihar Animal Sciences University, Patna)

## Slide 2: Anaerobic Biological Systems.
Anaerobic digestion (AD) is a biological process performed by an active microbial consortium in the absence of exogenous electron acceptors.
Anaerobic systems are generally seen as more economical for the biological stabilization of dairy wastes as they do not have the high-energy requirements associated with aeration in aerobic systems.
Anaerobic digestion also yields methane, which can be utilized as a heat or power source.
Furthermore, less sludge is generated, thereby reducing problems associated with sludge disposal. Nutrient requirements (N and P) are much lower than for aerobic systems.

## Slide 3: Anaerobic Biological Systems.
Pathogenic organisms are usually destroyed, and the final sludge has a high soil conditioning value if the concentration of heavy metals is low.
The possibility of treating high COD dairy wastes without previous dilution, as required by aerobic systems, reduces space requirements and the associated costs.
Bad odors are generally absent if the system is operated efficiently.
The disadvantages associated with anaerobic systems are the high capital cost, long startup periods, strict control of operating conditions, greater sensitivity to variable loads and organic shocks, as well as toxic compounds. The operational temperature must be maintained at about 33–37 C for efficient kinetics, because it is important to keep the pH at a value around 7, as a result of the sensitivity of the methanogenic population to low values.

## Slide 4: Anaerobic Biological Systems
In anaerobic breakdown of dairy wastewater, lactose is first fermented to lactic acid and fats and proteins are hydrolyzed to organic acids, amino acids, aldehydes, and alcohols. Second, the intermediate organic compounds are converted to methane and CO2. Because anaerobic digestion does not require oxygen for decomposition of organic material, operating costs for treatment are greatly reduced from that of aerobic treatments.
The anaerobic digester is a large fermentation tank in which fermentation, sludge settling, sludge digestion, and gas collection take place simultaneously. Many dairy plants use a two-stage system in which the first stage is complete mixing of the contents of a fermentation tank and the second stage is a digester in which the contents are allowed to stratify. The two-stage anaerobic process allows for higher loading rates and shorter hydraulic retention times.

## Slide 5: Anaerobic Methods
The anaerobic lagoon (anaerobic pond)
Completely stirred tank reactors (CSTR) are, next to lagoons, the simplest type of dry matter m3 /day and the digesters usually have capacities between 500 and 700 m3 . These reactors are normally used for concentrated wastes, especially those where the polluting matter is present mainly as suspended solids and has COD values of higher than 30,000 mg/L.
In the CSTR, there is no biomass retention; consequently, the HRT and sludge retention time (SRT) are not separated, necessitating long retention times that are dependent on the growth rate of the slowest-growing bacteria involved in the digestion process. Ross found that the HRT of the conventional digesters is equal to the SRT, which can range from 15–20 days. This type of digester has in the past been used by Lebrato et al. to treat cheese factory wastewater

## Slide 6: Anaerobic Methods
It is an anaerobic activated sludge process that consists of a completely mixed anaerobic reactor followed by some form of biomass separator. The separated biomass is recycled to the reactor, thus reducing the retention time from the conventional 20–30 days to ,1.0 day. Because the bacteria are retained and recycled, this type of plant can treat medium-strength wastewater (200–20,000 mg/L COD) very efficiently at high OLRs. The organic loading rate can vary from 1 to 6 kg/m3 day COD with COD removal efficiencies of 80–95%. The treatment temperature ranges from 30–40 C. A major difficulty encountered with this process is the poor settling properties of the anaerobic biomass from the digester effluent. The dairy wastewater was probably produced by a dairy with very good product-loss control and rather high water use.
The upflow anaerobic sludge blanket (UASB) reactor was developed for commercial purposes by Lettinga and coworkers at the Agricultural University in Wageningen, The Netherlands. It was first used to treat maize-starch wastewaters in South Africa, but its full potential was only realized after an impressive development program by Lettinga in the late 1970s. The rather simple design of the UASB bioreactor is based on the superior settling properties of granular sludge.

## Slide 7: Options of Treatments for a dairy Processing Plant
Treatment in nearby municipal treatment Plant facilities:
Limitations of handling certain flow rates and peak loads
Limitation of handling Fat in dairy wastes
Limitation of handling discharge regulations of dairy wastes due to limited capacities of treatment facilities
High sewer treatment charges depending upon flow rates, BOD5 , COD, Flow rates, SS and P contents etc.
Employing Waste disposal contractors for removal of semisolids and wastes from the sites:
Continuously impacted by increasing costs
Employing contractors for urgent removal of wastes is a limitation and problem
Control of BOD5, COD and SS as per regulation is stringent problem
Onsite Treatments of wastes in own Waste treatment Plant of Factory: Aerobic alone or Aerobic and Anaerobic combination:
Possible to control above limitation but sanitary discharges must be separate from organic dairy wastes
Generally preferable in a dairy plant

## Slide 8
THANK YOU