## Slide 1: Preventive and Breakdown Maintenance of Dairy Plants
Dr. J. Badshah
University Professor - cum - Chief Scientist
Dairy Engineering Department
Sanjay Gandhi Institute of Dairy Science & Technology, Jagdeopath, Patna
(Bihar Animal Sciences University, Patna)

## Slide 2: Corrective and Preventive Action
Corrective and Preventive actions are process of actions to be taken in equipments and machineries to avoid the undesirable conditions of sudden stoppage of production or service activities of plants. Its proper management is necessary to control the quality, safety and costs.
Actions required to correct the root cause of defects to avoid the recurrence are known as corrective actions. It actually occurs after the defects and breakdown have occurred in the plants and purpose of corrective action is to avoid the recurrence of the problems and to bring-up the plants in working condition again. Due to this, it is also known as Break down maintenance. It is necessary to identify the root causes.
Preventive actions/maintenances are the actions taken before occurrence to avoid the failures due to potential causes. It is done before occurrence and it is scheduled for identification and actions on potential risks. Potential risks may be out of any input resources such as man, machine, materials, methods, measurement and mother nature (i.e. 6Ms)

## Slide 3: When to carry out Breakdown maintenance and Preventive maintenance
Un-acceptable level quality, safety and non-conformance of standards of products and consumer rejection report: the root causes are identified and the equipment is dismantled and proper repairs, replacement and maintenance actions are taken.
Issues identified in internal audits such as process audits, machine audits, layout audits etc. the root causes are identified for corrective actions.
Adverse or unstable trends in production or service rendered by machines / equipments are reported in Statistical Quality Control (SQC) Processes. It results in rejection of products or services and root causes are identified to take corrective actions. It would avoid the recurrence of defects and controls the system and reduces the loss of time and costs.
To prevent the failures to come, potential sources of non-conformity are identified and maintenance are planned as a schedule through-out the year is preventive maintenance

## Slide 4: Planning of Plant Maintenance
Administrative Information: Purchase details, testing and commissioning services details, warranty & guarantee details of plant and machineries
Technical and Specific details of Equipments and Machineries: operational parameters, lubricants and utilities required
Inventory level requirement in stores specific to separate equipments/machines
Study of the performance of equipments and machines
Identifications of critical points
Check - up of different units and follow up the Preventive maintenance schedules
Frequency of check ups of the output products and services
Arrangement of electrical and mechanical workshops with maintenance teams to handle the situations of Breakdown maintenance, if any and also the Preventive maintenance as per the schedule.
Maintenance of power sources, distribution system, load scheduling for 24 hour period is planned to control load factor, power factor, efficiency of large motors, automations of machines.
Measurement of operational parameters in log book of each small and big equipments and machines is necessary for recording so that the problems can be identified and losses can be minimized.
Check the maintenance program includes the recommendations of Plant and energy audit teams.

## Slide 5: Principles of Preventive Maintenance
Routine External Check-ups: Vibration, Sound, heating
Periodic Internal Check-ups: Lubrication, minor adjustments, surface touch ups etc. after the equipment is shut down
Major Repairs/ Overhauling of machines: Prior to shut down, procurement of spares must be ensured, shut down available in lean seasons
Evaluating the Performance of equipments/machines: Frequency of evaluation through measurement and calibration of parameters is a matter of experience and performance evaluation is done based on log book entries.
Periodic Check ups of distribution lines of all utilities: leakages
Record Keeping and reporting by the operators: Records of operating parameters, malfunctioning and complaint records, lubrication records etc. To compare from Bench mark values/ Rated values of parameters.

## Slide 6: P.M. of Steam Boilers
Check the boiler blow down process.
Check the working of water level gauge glass indicator system.
Check the report of softener water and ensure that hardness not to exceed 10ppm.
Check the belt conveyor gear box oil level.
Check the coal bucket gear box oil level.
Steps to Improve Performance
Use variable speed drives on large boiler combustion air fans
Inspect oil heaters for proper oil temperatures
Clean burner, nozzles, strainers etc.
Establish a boiler efficiency maintenance Program
Follow the steps involved in preparation of boilers for statutory inspection
Start with energy audit and follow up program for energy conservation as well as improvement of boiler efficiency
Add an economizer for heating feed water and air preheater using waste heat of combustion flue gases

## Slide 7: P.M. of Refrigeration machines
Check the insulation of chilled water lines, cold storage and IBT
Timely and periodic air and oil purging from the system
It is advisable to segregate IBT, cold storage and Deep Freeze suction lines and connecting to separate refrigeration compressors
The refrigeration effect must be efficiently utilized by elimination of losses of chilled water and heat losses
Efficient running of refrigeration compressors and Preventive maintenance of compressors
Periodic cleaning of evaporators and condensors (0.8 mm scale built up on condenser tubes can increase energy consumption by 30-35%)
Night time running of compressors reduces the peak load and minimum KVA consumption and reduced electric bill
Timely preventive maintenance of compressors and systems
Minimizing reprocessing load to zero level.
Efficient running of cold storage, deep freeze and Ice-cream sections

## Slide 8: P.M. of Air Compressors and Submersible Pump for water
Adequate intake of filtered and cooled air.
Avoid leakages and maintain minimum pressure drops in air lines
Proper removal moisture from compressed air distribution system
Segregation of low and high pressure air requirements and Proper and effective maintenance of compressed air generation and distribution system
The primary maintenance items of inlet filter, oil drain, oil fill, motor greasing, condensate traps, and control calibration.
Each should be easily accessible. Service indicators help guarantee timely maintenance.
Synthetic lubricants must be replenished regularly provide superior lubricating characteristics, longer service life, and lower vaporization rates. Poly-glycols extend change-out intervals to 8,000 hours, have the lowest vaporization rate, and are biodegradable.
Oil-free compressors require limited amounts of lubricant for bearings and gears

## Slide 9: P. M. of Electrical Machines & Appliances
Maximum demand of electricity should be monitored properly to reduce the electric bill
Power factor should be controlled to near unity
Use energy efficient motors, equipments, transformers and othe appliances
Use of soft starters for heavy duty motors to improve power factor
Use of CFL/LED lighting devices
Multistage compression in case of high pressure ratio,
Selection of refrigerants – Eco-friendly Hydrocarbons and hydroflurocarbon (HFCs) are replacing fully halogenated (CFCs) Refrigerants.
Install variable frequency drive and monitor system performance.

## Slide 10: P.M. of Milk Processing and Manufacturing units in a Dairy Plants
Centrifugal Pump Maintenance: Locate the pump at a level below the liquid source for positive suction head. All piping and particulary suction line should have minimum length and minimum elbos and bends. Don’t throttle the suction line to control the capacity. Don’t start the pump with discharge full open, also in dry condition and without checking direction of rotation i.e. from motor side, the rotation should br clockwise. Mechanical seal and Pump casing O ring should be equal to at least nos. of pumps. If the pump does not generate the required discharge head rapidly, stop and repeat the priming operations.
HTST Milk pasteurizers: Periodic cleaning and maintenance of milk pasteurizers. Chilled milk pipe lines and holding section pipe line should be properly insulated. Milk pasteurizer temperature must be controlled properly with PID controller and FDV system to produce safe pasteurized milk and to avoid reprocessing. Plant regeneration efficiency should be monitored and controlled properly. Old milk pasteurization plant with poor regeneration efficiency, pinholes in plates and poor hygiene should be considered for replacement.

## Slide 11: Piping installations
Pipes must be supported independently avoiding causing stresses on the pumps.
Internal diameter must be of the same size as that of pump connection. If the pipe diameter changes along the suction line use reduction cones in such a way that slope is towards down stream and no air pocket is formed.
The suction pipe must be as short as possible. The maximum velocity in suction pipe should not be greater than 3 m/s (Most recommended is 2-3 m/s). The suction pipe must be designed in such a way to prevent air from entering the pump.
Fit expansion joint in case of hot liquid transportation in pipes to compensate any expansion of the pipe.

## Slide 12: P.M. of Manufacturing Units..contd.
Ghee is made in dairy plant from butter or directly from cream. Clarification of butter in ghee kettle requires high amount of steam because butter contains 16 % moisture. Instead of this procedure a large portion of water can be removed by centrifuging the melted butter and then clarifying in the ghee kettle. It can save steam and time and also would improve the capacity of plant. The heat of already clarified ghee can be used to melt the butter.
Use of Scraped surface heat exchanger system for forewarming and concentration of milk to prepare small scale and economized condensed milk and indigenous dairy products for energy saving and quality production.
Use of Non- thermal technologies such as Membrane technologies in milk processing, High Hydrostatic pressure technology for cold processing, Superfluid extraction technology, Eco friendly packages for dairy products, pulsed electric field technology, Nano technology for nano food and intelligent packaging etc. are the scope for producing qualitative and functional safe foods by optimizing energy consumption (Minz, et. al, 2010).

## Slide 13: P.M. of Condensing and Drying Plants
5-effects evaporator with TVR: 8 kg water evapn per kg steam
7 –effects evaporator with TVR: 10 kg water evapn. Per kg steam
Multiple effects evaporator without condenser with MVR: Low steam consumption in comparison to equivalent evaporator with TVR and no cooling water requirement.
Use of multipass construction in each effect to retain the advantages of tube wetting rate for different products to make flexible.
Higher degree of automation gives higher quality with lower cost.
Full automation of spray dryers and feed treatment to control moisture content in the powder and also to control quality of powder including avoiding burnt particle and safety of drying chamber must be provided in the system. This may be done by feed rate regulation through servomotor and positive pumps or by air heater regulation.
Three stage dryer efficiency increases by 20 percent from 35 % to 55%.
To reduce stack losses, bag filter, cyclone separator and wet scrubbers etc. should be efficiently designed and installed. Their efficiency should be checked regularly.

## Slide 14: P.M. of solar energy modules installed in plants
Solar energy can be used for hot water generation for milk pasteurization and CIP
To install fully self tracking parabolic solar concentrator for generation of hot water and storage in a tank to save furnace oil used for boiler
Biofuels offer a sustainable and cleaner source of power, with significantly lower green house gas emissions.
Biomass (wood waste/agricultural residues etc.) gasifier has high potential for production of low calorific value gas for small scale agro based industries for thermal energy and electricity applications.
Solar electric also known as photo voltaic cells that convert sunlight directly into electricity for lighting, battery charging, small motors, water pumping and electric fences etc.

## Slide 15: P.M. of Effluent Treatment Plants
There is considerable scope of energy conservation, if effluent generation and treatment are given due attention
Segregate low BOD and High BOD streams to save energy and land for aeration lagoons in aerobic digestion
The combination of anaerobic cum aerobic treatment plants offers huge savings
For water recycling and reuse, the concept of tertiary treatment to give good quality water should be adopted
Use of Upflow Anaerobic Sludge Blanket (UASB) technology followed by Aerobic treatment saves not only energy consumption and energy cost but also produce bio gas. Methane/bio gas can be used to generate electricity which further reduces the operating and thereby production cost of product.
Biomethanation of dairy effluent is an anaerobic treatment process of dairy effluent to remove the organic substances and to convert them into methane rich biogas. The methane content in the biogas is 65%. The reactor can tolerate an organic loading of 10 kg COD/ cubic meter reactor volume / day. Methane rich gas is produced through this process and can be utilized for thermal applications and power generation as well (Rathore, 2010).

## Slide 16: Maintenance of Milk Pouch Filling Machine
Dismantle both fixed and mounting horizontal jaws for cleaning the electrodes. The use of a hand brush with trichloroethane is recommended.
It is to be remembered that rubber linings are to be changed for every 40,000 pouches.
Check the condition of Teflon, rubber lining and sealing wire.
When changing the adhesive Teflon, do not forget to disconnect the sealing wire to remove any cooked milk that could be found.
Change the oil/grease in the gearbox after every 2,000 hr of operation
Low air pressure (6 kg/cm2), Worn out O rings in horizontal seal cylinder , Jaw pressures adjusted too low and will cause horizontal seal leaks.
Corner seepers are very small leaks at very corner of the horizontal seal. Which is due to compression of the pouch in the crates. Proper maintenance of horizontal sealing and back-up bars is to be followed.

## Slide 17: Vertical seal leaks in Pouches
Weak Seals are caused due to lack of heat , which may be due to:
Too low a setting on the vertical seal adjustment
Poor sealing relay contacts
Poor electrical connections
Poor contact on rheostat controls
Increase in flow rate of cooling water
Pin hole and Burn holes caused Due to too much heat or little pressure on the vertical seal. Burn holes appear only when vertical seals overlap.

## Slide 18
THANK YOU